## generationrptforNTPCStation
CENTRAL ELECTRICITY AUTHORITY G O & D WING OPERATION PERFORMANCE MONITORING DIVISION
GENERATION REPORT FOR NTPC STATIONS DATED - 10-Apr-2025
Power Station | Monitored Cap. (MW) | Available Cap. (MW) | Generation (MU) |  |  |  | Coal Stock In day's | Cap. Under Outage (MW) | Maintenance Start Date (dd/mm/yyyyhh24:mi) | Expected Returned Date/SyncDate | Remarks
|  |  | Today's Program | Today's Actual | April 1 Till Date
[5 empty] | Prog. | Actual
Haryana
FARIDABAD CCPP | 431.59 | 293.83 | 0.6 | 0 | 6 | 0 |  | 137.76
Total THER (GT) | 431.59 | 293.83 | 0.6 | 0 | 6 | 0 |  | 137.76
Total Generation | 431.59 | 293.83 | 0.6 | 0 | 6 | 0 |  | 137.76
Himachal Pradesh
KOLDAM | 800 | 600 | 4.43 | 5.23 | 44.3 | 35.53 |  | 200
Total HYDRO | 800 | 600 | 4.43 | 5.23 | 44.3 | 35.53 |  | 200
Total Generation | 800 | 600 | 4.43 | 5.23 | 44.3 | 35.53 |  | 200
Rajasthan
ANTA CCPP | 419.33 | 0 | 1.1 | 0 | 11 | 3.14 |  | 419.33
Total THER (GT) | 419.33 | 0 | 1.1 | 0 | 11 | 3.14 |  | 419.33
Total Generation | 419.33 | 0 | 1.1 | 0 | 11 | 3.14 |  | 419.33
Uttarakhand
TAPOVAN VISHNUGAD HPS | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Total HYDRO | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Total Generation | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Uttar Pradesh
DADRI (NCTPP) | 1820 | 1820 | 33.56 | 28.19 | 335.6 | 269.4 | 162 | 0
Unit 1 | 210 | 210 | 3.97 | 3.16 | 39.7 | 32.47 | 27 | 0
Unit 2 | 210 | 210 | 4.1 | 3.6 | 41 | 32.77 | 27 | 0
Unit 3 | 210 | 210 | 3.73 | 3.17 | 37.3 | 32.75 | 27 | 0
Unit 4 | 210 | 210 | 3.73 | 3.1 | 37.3 | 31.93 | 27 | 0
Unit 5 | 490 | 490 | 8.83 | 7.5 | 88.3 | 58.74 | 27 | 0
Unit 6 | 490 | 490 | 9.2 | 7.66 | 92 | 80.74 | 27 | 0
RIHAND STPS | 3000 | 2500 | 67.93 | 61.15 | 679.3 | 659.19 | 126 | 500
Unit 1 | 500 | 0 | 11.3 | 8.28 | 113 | 107.88 | 21 | 500 | 2025-04-10 19:22 |  | TUBE LKG. AT LOW TEMP. SUPERHEATER ZONE
Unit 2 | 500 | 500 | 11.3 | 10.55 | 113 | 109.17 | 21 | 0
Unit 3 | 500 | 500 | 11.3 | 10.63 | 113 | 111.81 | 21 | 0
Unit 4 | 500 | 500 | 11.4 | 10.46 | 114 | 107.84 | 21 | 0
Unit 5 | 500 | 500 | 11.3 | 10.61 | 113 | 111.39 | 21 | 0
Unit 6 | 500 | 500 | 11.33 | 10.62 | 113.3 | 111.1 | 21 | 0
SINGRAULI STPS | 2000 | 2000 | 45.13 | 43.12 | 451.3 | 393.1 | 154 | 0
Unit 1 | 200 | 200 | 4.53 | 4.42 | 45.3 | 44.88 | 22 | 0
Unit 2 | 200 | 200 | 4.47 | 4.43 | 44.7 | 44.94 | 22 | 0
Unit 3 | 200 | 200 | 4.5 | 4.44 | 45 | 43.96 | 22 | 0
Unit 4 | 200 | 200 | 4.47 | 4.42 | 44.7 | 44.97 | 22 | 0
Unit 5 | 200 | 200 | 4.53 | 4.42 | 45.3 | 44.45 | 22 | 0
Unit 6 | 500 | 500 | 11.33 | 10.39 | 113.3 | 62.1 | 22 | 0
Unit 7 | 500 | 500 | 11.3 | 10.6 | 113 | 107.8 | 22 | 0
TANDA TPS | 1760 | 1100 | 34.57 | 27.95 | 345.7 | 347.7 | 186 | 660
Unit 1 | 110 | 110 | 1.9 | 2.12 | 19 | 21.24 | 31 | 0
Unit 2 | 110 | 110 | 1.9 | 2.13 | 19 | 21.59 | 31 | 0
Unit 3 | 110 | 110 | 1.9 | 2.16 | 19 | 19.57 | 31 | 0
Unit 4 | 110 | 110 | 1.77 | 2.17 | 17.7 | 21.83 | 31 | 0
Unit 5 | 660 | 0 | 13.83 | 6.22 | 138.3 | 128.5 | 31 | 660 | 2025-04-10 10:39 |  | A.V.R. PROBLEM
Unit 6 | 660 | 660 | 13.27 | 13.15 | 132.7 | 134.97 | 31 | 0
UNCHAHAR TPS | 1550 | 1550 | 31.47 | 27.05 | 314.7 | 291.84 | 84 | 0
Unit 1 | 210 | 210 | 3.93 | 3.52 | 39.3 | 39.36 | 14 | 0
Unit 2 | 210 | 210 | 4.17 | 3.46 | 41.7 | 38.33 | 14 | 0
Unit 3 | 210 | 210 | 4.4 | 3.59 | 44 | 39.22 | 14 | 0 | 2025-04-10 22:29 |  | P.A. FANS PROBLEM
Unit 4 | 210 | 210 | 4.47 | 3.91 | 44.7 | 37.11 | 14 | 0
Unit 5 | 210 | 210 | 4.47 | 3.66 | 44.7 | 40.49 | 14 | 0
Unit 6 | 500 | 500 | 10.03 | 8.91 | 100.3 | 97.33 | 14 | 0
Total THERMAL | 10130 | 8970 | 212.66 | 187.46 | 2126.6 | 1961.23 | 712 | 1160
AURAIYA CCPP | 663.36 | 0 | 2.53 | 0 | 25.3 | 5.11 |  | 663.36
DADRI CCPP | 829.78 | 0 | 3.13 | 0 | 31.3 | 4.93 |  | 829.78
Total THER (GT) | 1493.14 | 0 | 5.66 | 0 | 56.6 | 10.04 |  | 1493.14
Total Generation | 11623.14 | 8970 | 218.32 | 187.46 | 2183.2 | 1971.27 | 712 | 2653.14
Chhatisgarh
KORBA STPS | 2600 | 2600 | 59.27 | 56.44 | 592.7 | 576.91 | 119 | 0
Unit 1 | 200 | 200 | 4.53 | 4.45 | 45.3 | 46.48 | 17 | 0
Unit 2 | 200 | 200 | 4.53 | 4.44 | 45.3 | 46.24 | 17 | 0
Unit 3 | 200 | 200 | 4.57 | 4.5 | 45.7 | 46.95 | 17 | 0
Unit 4 | 500 | 500 | 11.3 | 10.85 | 113 | 112.91 | 17 | 0
Unit 5 | 500 | 500 | 11.4 | 10.56 | 114 | 94.96 | 17 | 0
Unit 6 | 500 | 500 | 11.47 | 10.85 | 114.7 | 114.74 | 17 | 0
Unit 7 | 500 | 500 | 11.47 | 10.79 | 114.7 | 114.63 | 17 | 0
LARA TPP | 1600 | 1600 | 36.74 | 35.16 | 367.4 | 372.59 | 24 | 0
Unit 1 | 800 | 800 | 18.37 | 17.34 | 183.7 | 184.82 | 12 | 0
Unit 2 | 800 | 800 | 18.37 | 17.82 | 183.7 | 187.77 | 12 | 0
SIPAT STPS | 2980 | 2480 | 66.68 | 50.02 | 666.8 | 529.95 | 130 | 500
Unit 1 | 660 | 660 | 14.77 | 14.12 | 147.7 | 150.16 | 26 | 0
Unit 2 | 660 | 660 | 14.87 | 13.98 | 148.7 | 150.21 | 26 | 0
Unit 3 | 660 | 660 | 14.7 | 11.26 | 147 | 117.48 | 26 | 0 | 2025-04-08 00:47 | 2025-04-10 02:12 | AIR PREHEATERS PROBLEM
Unit 4 | 500 | 0 | 11.17 | 0 | 111.7 | 0 | 26 | 500 | 2025-03-16 00:22 |  | BOILER OVERHAUL/ ANNUAL MAINTENANCE
Unit 5 | 500 | 500 | 11.17 | 10.66 | 111.7 | 112.1 | 26 | 0
Total THERMAL | 7180 | 6680 | 162.69 | 141.62 | 1626.9 | 1479.45 | 273 | 500
Total Generation | 7180 | 6680 | 162.69 | 141.62 | 1626.9 | 1479.45 | 273 | 500
Gujarat
GANDHAR CCPP | 657.39 | 0 | 2.64 | 0 | 26.4 | 9.27 |  | 657.39
KAWAS CCPP | 656.2 | 0 | 2.06 | 0 | 16.73 | 8.78 |  | 656.2
Total THER (GT) | 1313.59 | 0 | 4.7 | 0 | 43.13 | 18.05 |  | 1313.59
Total Generation | 1313.59 | 0 | 4.7 | 0 | 43.13 | 18.05 |  | 1313.59
Madhya Pradesh
GADARWARA TPP | 1600 | 1600 | 16.17 | 26.26 | 161.7 | 311.49 | 30 | 0
Unit 1 | 800 | 800 | 0 | 13.31 | 0 | 154.47 | 15 | 0
Unit 2 | 800 | 800 | 16.17 | 12.95 | 161.7 | 157.02 | 15 | 0 | 2025-04-10 22:59 |  | GENERATOR PROTECTION
KHARGONE STPP | 1320 | 1320 | 24.57 | 20.93 | 245.7 | 234.81 | 30 | 0
Unit 1 | 660 | 660 | 12.4 | 10.46 | 124 | 116.14 | 15 | 0
Unit 2 | 660 | 660 | 12.17 | 10.47 | 121.7 | 118.67 | 15 | 0
VINDHYACHAL STPS | 4760 | 4760 | 109.23 | 99.85 | 1092.3 | 1002.48 | 234 | 0
Unit 1 | 210 | 210 | 4.87 | 4.52 | 48.7 | 45.24 | 18 | 0
Unit 10 | 500 | 500 | 11.4 | 10.49 | 114 | 109.91 | 18 | 0
Unit 11 | 500 | 500 | 11.57 | 10.52 | 115.7 | 109.55 | 18 | 0
Unit 12 | 500 | 500 | 11.5 | 10.48 | 115 | 108.89 | 18 | 0
Unit 13 | 500 | 500 | 11.43 | 10.27 | 114.3 | 107.41 | 18 | 0
Unit 2 | 210 | 210 | 4.83 | 4.33 | 48.3 | 44.92 | 18 | 0
Unit 3 | 210 | 210 | 4.83 | 4.39 | 48.3 | 10.96 | 18 | 0
Unit 4 | 210 | 210 | 4.83 | 4.49 | 48.3 | 46.64 | 18 | 0
Unit 5 | 210 | 210 | 4.83 | 4.38 | 48.3 | 46.27 | 18 | 0
Unit 6 | 210 | 210 | 4.87 | 4.45 | 48.7 | 46.73 | 18 | 0
Unit 7 | 500 | 500 | 11.47 | 10.44 | 114.7 | 105.1 | 18 | 0
Unit 8 | 500 | 500 | 11.4 | 10.61 | 114 | 110.92 | 18 | 0
Unit 9 | 500 | 500 | 11.4 | 10.48 | 114 | 109.94 | 18 | 0
Total THERMAL | 7680 | 7680 | 149.97 | 147.04 | 1499.7 | 1548.78 | 294 | 0
Total Generation | 7680 | 7680 | 149.97 | 147.04 | 1499.7 | 1548.78 | 294 | 0
Maharashtra
MAUDA TPS | 2320 | 1160 | 46.06 | 27.69 | 460.6 | 363.92 | 124 | 1160
Unit 1 | 500 | 0 | 9.83 | 7.2 | 98.3 | 96.84 | 31 | 500 | 2025-04-10 17:59 | 2025-04-10 20:21 | C&I PROBLEM
Unit 2 | 500 | 500 | 9.83 | 8.84 | 98.3 | 98.93 | 31 | 0
Unit 3 | 660 | 660 | 13.1 | 11.65 | 131 | 132.35 | 31 | 0
Unit 4 | 660 | 0 | 13.3 | 0 | 133 | 35.8 | 31 | 660 | 2025-04-09 09:22 |  | REHEATER TUBE LEAKAGE
SOLAPUR STPS | 1320 | 1320 | 22 | 19.66 | 220 | 209.25 | 28 | 0
Unit 1 | 660 | 660 | 11.17 | 9.81 | 111.7 | 108.34 | 14 | 0
Unit 2 | 660 | 660 | 10.83 | 9.85 | 108.3 | 100.91 | 14 | 0
Total THERMAL | 3640 | 2480 | 68.06 | 47.35 | 680.6 | 573.17 | 152 | 1160
Total Generation | 3640 | 2480 | 68.06 | 47.35 | 680.6 | 573.17 | 152 | 1160
Andhra Pradesh
SIMHADRI | 2000 | 2000 | 39.31 | 36.46 | 393.1 | 397.12 | 36 | 0
Unit 1 | 500 | 500 | 9.57 | 9.19 | 95.7 | 102.11 | 9 | 0
Unit 2 | 500 | 500 | 9.67 | 9.16 | 96.7 | 98.01 | 9 | 0
Unit 3 | 500 | 500 | 10.17 | 9.1 | 101.7 | 100.28 | 9 | 0
Unit 4 | 500 | 500 | 9.9 | 9.01 | 99 | 96.72 | 9 | 0
Total THERMAL | 2000 | 2000 | 39.31 | 36.46 | 393.1 | 397.12 | 36 | 0
Total Generation | 2000 | 2000 | 39.31 | 36.46 | 393.1 | 397.12 | 36 | 0
Karnataka
KUDGI STPP | 2400 | 2400 | 39.77 | 35.45 | 397.7 | 371.81 | 42 | 0
Unit 1 | 800 | 800 | 13.07 | 11.85 | 130.7 | 123.77 | 14 | 0
Unit 2 | 800 | 800 | 13.67 | 11.77 | 136.7 | 124.07 | 14 | 0
Unit 3 | 800 | 800 | 13.03 | 11.83 | 130.3 | 123.97 | 14 | 0
Total THERMAL | 2400 | 2400 | 39.77 | 35.45 | 397.7 | 371.81 | 42 | 0
Total Generation | 2400 | 2400 | 39.77 | 35.45 | 397.7 | 371.81 | 42 | 0
Kerala
R. GANDHI CCPP (Liq.) | 359.58 | 0 | 0 | 0 | 0 | 0 |  | 359.58
Total THER (GT) | 359.58 | 0 | 0 | 0 | 0 | 0 |  | 359.58
Total Generation | 359.58 | 0 | 0 | 0 | 0 | 0 |  | 359.58
Telangana
RAMAGUNDEM STPS | 2600 | 2600 | 55.73 | 42.82 | 557.3 | 462.05 | 182 | 0
Unit 1 | 200 | 200 | 4.3 | 3.34 | 43 | 37.83 | 26 | 0
Unit 2 | 200 | 200 | 4.3 | 3.33 | 43 | 37.99 | 26 | 0
Unit 3 | 200 | 200 | 4.3 | 3.27 | 43 | 37.37 | 26 | 0
Unit 4 | 500 | 500 | 10.43 | 8.17 | 104.3 | 93.18 | 26 | 0
Unit 5 | 500 | 500 | 10.9 | 8.07 | 109 | 64.89 | 26 | 0
Unit 6 | 500 | 500 | 10.6 | 8.27 | 106 | 94 | 26 | 0
Unit 7 | 500 | 500 | 10.9 | 8.37 | 109 | 96.79 | 26 | 0
TELANGANA STPP PH-1 | 1600 | 1600 | 31.27 | 29.94 | 312.7 | 321.78 | 66 | 0
Unit 1 | 800 | 800 | 15.67 | 14.99 | 156.7 | 161.17 | 33 | 0
Unit 2 | 800 | 800 | 15.6 | 14.95 | 156 | 160.61 | 33 | 0
Total THERMAL | 4200 | 4200 | 87 | 72.76 | 870 | 783.83 | 248 | 0
Total Generation | 4200 | 4200 | 87 | 72.76 | 870 | 783.83 | 248 | 0
Bihar
BARAUNI TPS | 710 | 250 | 10.66 | 5.88 | 106.6 | 87.92 | 188 | 460
Unit 6 | 105 | 0 | 0 | 0 | 0 | 0 | 47 | 105 | 2023-07-22 12:05 |  | UNIT LIKELY TO BE SCRAPPED.
Unit 7 | 105 | 0 | 0 | 0 | 0 | 0 | 47 | 105 | 2023-07-19 15:30 |  | UNIT LIKELY TO BE SCRAPPED.
Unit 8 | 250 | 0 | 5.23 | 1.43 | 52.3 | 39.88 | 47 | 250 | 2025-04-07 21:56 | 2025-04-10 15:22 | TUBE LKG. AT LOW TEMP. SUPERHEATER ZONE
Unit 9 | 250 | 250 | 5.43 | 4.45 | 54.3 | 48.04 | 47 | 0
BARH STPS | 2640 | 2640 | 62.14 | 52.83 | 621.4 | 505.02 | 165 | 0
Unit 1 | 660 | 660 | 12 | 13.41 | 120 | 91.21 | 33 | 0
Unit 2 | 660 | 660 | 10.67 | 12.88 | 106.7 | 133 | 33 | 0
Unit 3 | 0 | 0 | 11.57 | 0 | 115.7 | 0 | 33 | 0 |  |  | unit not yet commissioned
Unit 4 | 660 | 660 | 14 | 13.43 | 140 | 140.86 | 33 | 0
Unit 5 | 660 | 660 | 13.9 | 13.11 | 139 | 139.95 | 33 | 0
KAHALGAON TPS | 2340 | 2340 | 50.25 | 47 | 502.5 | 497.53 | 154 | 0
Unit 1 | 210 | 210 | 4.63 | 4.18 | 46.3 | 44.96 | 22 | 0
Unit 2 | 210 | 210 | 4.5 | 3.81 | 45 | 41.62 | 22 | 0
Unit 3 | 210 | 210 | 4.5 | 4.21 | 45 | 45.15 | 22 | 0
Unit 4 | 210 | 210 | 4.63 | 4.11 | 46.3 | 43.69 | 22 | 0
Unit 5 | 500 | 500 | 10.53 | 10.14 | 105.3 | 107.01 | 22 | 0
Unit 6 | 500 | 500 | 10.53 | 10.27 | 105.3 | 107.49 | 22 | 0
Unit 7 | 500 | 500 | 10.93 | 10.28 | 109.3 | 107.61 | 22 | 0
Total THERMAL | 5690 | 5230 | 123.05 | 105.71 | 1230.5 | 1090.47 | 507 | 460
Total Generation | 5690 | 5230 | 123.05 | 105.71 | 1230.5 | 1090.47 | 507 | 460
Jharkhand
NORTH KARANPURA TPP | 1320 | 1320 | 36.56 | 28.15 | 365.6 | 227.24 | 102 | 0
Unit 1 | 660 | 660 | 13.53 | 14.08 | 135.3 | 82.18 | 34 | 0
Unit 2 | 660 | 660 | 13.53 | 14.07 | 135.3 | 145.06 | 34 | 0
Unit 3 | 0 | 0 | 9.5 | 0 | 95 | 0 | 34 | 0 |  |  | unit not yet commissioned
Total THERMAL | 1320 | 1320 | 36.56 | 28.15 | 365.6 | 227.24 | 102 | 0
Total Generation | 1320 | 1320 | 36.56 | 28.15 | 365.6 | 227.24 | 102 | 0
Odisha
DARLIPALI STPS | 1600 | 800 | 36.44 | 27.54 | 364.4 | 367.93 | 28 | 800
Unit 1 | 800 | 800 | 18.07 | 18.63 | 180.7 | 189.22 | 14 | 0
Unit 2 | 800 | 0 | 18.37 | 8.91 | 183.7 | 178.71 | 14 | 800 | 2025-04-10 11:28 |  | SUPER HEATER TUBE LEAKAGE
TALCHER STPS | 3000 | 3000 | 67.79 | 63.44 | 677.9 | 637.84 | 90 | 0
Unit 1 | 500 | 500 | 11.43 | 10.39 | 114.3 | 77.57 | 15 | 0
Unit 2 | 500 | 500 | 11.1 | 10.56 | 111 | 110.58 | 15 | 0
Unit 3 | 500 | 500 | 11.53 | 10.64 | 115.3 | 112.47 | 15 | 0
Unit 4 | 500 | 500 | 11.4 | 10.59 | 114 | 112.32 | 15 | 0
Unit 5 | 500 | 500 | 11.1 | 10.69 | 111 | 112.65 | 15 | 0
Unit 6 | 500 | 500 | 11.23 | 10.57 | 112.3 | 112.25 | 15 | 0
Total THERMAL | 4600 | 3800 | 104.23 | 90.98 | 1042.3 | 1005.77 | 118 | 800
Total Generation | 4600 | 3800 | 104.23 | 90.98 | 1042.3 | 1005.77 | 118 | 800
West Bengal
FARAKKA STPS | 2100 | 1900 | 44.55 | 33.86 | 445.5 | 345.82 | 204 | 200
Unit 1 | 200 | 0 | 4.17 | 0 | 41.7 | 7.67 | 34 | 200 | 2025-04-03 18:48 |  | SEAL OIL SYSTEM PROBLEM
Unit 2 | 200 | 200 | 4.17 | 3.9 | 41.7 | 13.87 | 34 | 0
Unit 3 | 200 | 200 | 4.37 | 3.56 | 43.7 | 40.3 | 34 | 0
Unit 4 | 500 | 500 | 10.37 | 8.05 | 103.7 | 89.52 | 34 | 0
Unit 5 | 500 | 500 | 10.77 | 8.56 | 107.7 | 92.36 | 34 | 0
Unit 6 | 500 | 500 | 10.7 | 9.79 | 107 | 102.1 | 34 | 0
Total THERMAL | 2100 | 1900 | 44.55 | 33.86 | 445.5 | 345.82 | 204 | 200
Total Generation | 2100 | 1900 | 44.55 | 33.86 | 445.5 | 345.82 | 204 | 200
Assam
BONGAIGAON TPP | 750 | 500 | 10.47 | 8.7 | 104.7 | 95.76 | 147 | 250
Unit 1 | 250 | 250 | 5.27 | 4.36 | 52.7 | 47.86 | 49 | 0
Unit 2 | 250 | 250 | 5.2 | 4.34 | 52 | 47.9 | 49 | 0
Unit 3 | 250 | 0 | 0 | 0 | 0 | 0 | 49 | 250 | 2025-02-25 00:34 |  | OVERHAULING WORKS
Total THERMAL | 750 | 500 | 10.47 | 8.7 | 104.7 | 95.76 | 147 | 250
Total Generation | 750 | 500 | 10.47 | 8.7 | 104.7 | 95.76 | 147 | 250